## Legend
| Fixture Code Legend and Notes |  |  |  |  | (revised 12/14/07)*
Fixture Code Explanations
Fixture Type |  |  |  | Ballast Type
| C | Canopy fixture with LED Array |  | for fluorescent fixtures
| CF | Compact Fluorescent |  |  | IxL | Electronic, Instant start - IS (x = lamp code)
| CFC | Compact Fluorescent, Cold Cathode |  |  | xL | Electronic, Rapid start - RS (x = lamp code)
| CFD | Compact Fluorescent, double-D Shape |  |  | GxL | Electronic, Programmed start or Programmed rapid start - PRS (x = lamp code)
| CFG | Compact Fluorescent, GU24 LVS Socket
| CFM | Compact Fluorescent, Multi tube |  |  | S | Standard magnetic
| CFT | Compact Fluorescent, Twin tube |  |  | E | EPACT Energy efficient magnetic [Note 2]
|  | (including “Biaxial” fixtures) |  |  | U | Premium ballast
| CFQ | Compact Fluorescent, Quad tube |  | for Metal Halide Fixtures
| ECF | Exit sign, Compact Fluorescent |  |  | CWA | Constant Wattage Autotransformer - magnetic
| EF | Exit sign, linear Fluorescent (T5, T1) |  |  | RL | Regulated Lag - magnetic
| EI | Exit sign, Incandescent |  |  | LR | Linear Reactor - magnetic
| ELED | Exit sign, LED |  |  | L | electronic low frequency (w/PS or Ceramic lamps)
| F | Fluorescent, linear
| FC | Fluorescent, Circline |  | Configuration [letter]
| FEI | Fluorescent, Electrodeless Induction |  |  | T | Tandem wired fixture
| FU | Fluorescent, U-tube |  |  | D | Delamped fixture, i.e. some lamps permanently removed but ballasts remain and are energized
| H | Halogen incandescent
| HLV | Halogen Low Voltage
| HPS | High Pressure Sodium |  | Configuration [number]
| I | Incandescent |  | for de-lamped fixtures
| LED | Light Emitting Diode (LED) traffic signal |  |  | Number signifies the number of energized ballasts in a delamped fixture: e.g. An “F42EE/D2” is an “F44EE” with two lamps removed and two energized ballasts; or it could signify an “F43EE” with one lamp removed and two energized ballasts. The configuration code cannot differentiate between energized ballasts controlling no (0) lamps and those controlling one or two lamps for the examples cited: e.g. an F42EE/D2 can be set up to have one ballast controlling two lamps and one energized ballast controlling no lamps, or both ballasts control one lamp each.
| LEDO | Light Emitting Diode (LED) fixtures - Other
| MH | Metal Halide
| MV | Mercury Vapor
| SCRW | Screw-In lamp/base w/ permanent locking device [Note 1]
| WP | Wall Pack fixture with LED Array
Lamp Type
for fluorescent fixtures
| A | T12, “F25T12” type—25 watt, 4 ft |  | for tandem wired ballasts
| B | T5, “Biaxial” twin tube for compact fluorescent |  |  | Number signifies the total number of lamps being run by the ballast: e.g. An “F42LL/T4” would indicate that a four-lamp ballast is wired to run two two-lamp fixtures.
| L | T8, bipin, for Instant Start or Rapid Start ballast
| E | T12, bipin, EPACT energy efficient [Note 2]
| EH | T12, EPACT, High output lamp (800mA) |  | with no preceding letter
| EI | T12, EPACT, 4ft or 8ft, single pin Instant start lamp |  |  | Number indicates the number of ballasts in an ambiguous multiple ballast fixture: e.g. An “F43ILL/2” indicates a three-lamp fixture with two instant start ballasts (as is often the case if there is A/B switching).
| EL | T8, reduced wattage 4 ft, 30 watt
| EV | T12, EPACT, Very high output (1500mA)
| NL | T8, reduced wattage 4 ft, 25 watt
| P | T5, linear, 2-5ft lengths |  | Ballast Light Output (ballast factors are approximate ranges)
| PH | T5, linear high output lamp |  |  | "_" | No character - Normal light output or NLO (0.85<BF<0.95)
| RL | T8, reduced wattage 4 ft, 28 watt |  |  | VR | Very Reduced light output or VRLO (BF<0.70)
| S | T12, bipin, Standard wattage |  |  | R | Reduced light output or RLO (0.70<BF<0.85)
| SI | T12, Standard, single pin, Instant start lamp |  |  | H | High light output or HLO (0.95<BF<1.1)
| SH | T12, Standard, High output lamp |  |  | V | Very high light output or VHLO (BF>1.1)
| SV | T12, Standard, Very high output lamp |  | Fixture Code Notes:
| T | T10 lamp | 1) | "SCRW" Screw-in lamp/Base designation includes both 1-piece integrated ballast and 2-piece modular screw-in ballast systems. Both require the use of a permanent locking device (Anti-theft devices using a key-removable insert are not eligible).
for LED traffic signals, Other LED and Neon
| 12GA | 12” Green Arrow
| 12RA | 12” Red Arrow | 2) | Lamp/ballast combinations that are non-EPACT compliant are assigned EPACT demand values. Thus, fixtures with 40-watt T12 lamps and std-magnetic ballasts are assigned the baseline value for an 'EE' type fixture w/ 34-watt T12 energy efficient lamps w/ energy efficient magnetic ballasts-i.e. use F44EE instead of 'ES', 'SE' or 'SS'.
| 12RB | 12” Red Ball
| 8GB | 8” Green Ball
| 8RB | 8” Red Ball
| F | Filled fixture (ex. LEDPH16OF) | 3) | Pedestrian signal fixture wattage only refers to wattage of the particular phase – i.e. Pedestrian Person phase may be different from Pedestrian Hand phase for an overlay type fixture.
| O | Overlay (ex. LEDPH16OF)
| O | Outline fixture (ex. LEDPH16OO)
| PH | Pedestrian Hand signal (ex. LEDPH16OO) [Note 3] |  | Wattage Table Notes:
| PP | Pedestrian Person Signal (ex. LEDPP12SF) [Note 3] | 4) | Newly added or modified Fixture codes and Watt/Fixt values are denoted in bold lettering within the Wattage Table.
| S | Side by Side fixture (ex. LEDPH16SO)
for Other LED and Neon |  |  | 5) | The Column labeled Watts/Fixture in the Wattage Table includes ballast loads.
| BG | Blue Green LED lamp | 6) | The fixture wattages represent an average value, rounded to nearest whole watt.
| BL | Blue LED lamp | 7) | Multilamp incandescent, screw-in CFL, halogen, metal halide and mercury vapor fixtures were removed from the Table for simplification. Sponsors should therefore use multiples of the corresponding single-lamp fixtures to fill out inventory forms - i.e. (1) I100/5 fixture should now be represented by (5) I100/1 fixtures.
| G | Green LED lamp
| NEON | NEON illuminated sign, magnetic or electronic ballast
| OR | Orange Red LED lamp
| R | Red LED lamp
| W | White LED (RGB or 'Lunar' Blue White) lamp | * | Highlighted areas of the Legend denote changes or additions to the previous Wattage Table version
| Y | Yellow LED lamp